# User Manual: Digital Motor Starter with GSM Integration

## 1. COVER PAGE

This Technical Reference Manual serves as the definitive guide for the installation, configuration, and operation of the Digital Motor Starter with GSM Integration. This document is intended for electrical engineers and industrial operators to ensure the precise deployment of the device's embedded firmware logic.

# Digital Motor Starter with GSM Integration

### Advanced Industrial Motor Controller with 8-bit Microchip® PIC18F Architecture

Model: QBIT-PIC18F-GSM

Remote Control, Intelligent Protection, and Real-Time Monitoring

The QBIT-PIC18F-GSM utilizes high-speed microcontroller logic to manage industrial motor assets. Before proceeding, it is mandatory to review the safety protocols in Section 2, as high-voltage equipment requires strict adherence to operational standards.

--------------------------------------------------------------------------------

## 2. SAFETY WARNINGS

Adherence to these safety standards is non-negotiable. The high-voltage industrial environment poses extreme risks to personnel and hardware. Failure to follow these mandates will void the warranty and may result in catastrophic equipment failure.

- WARNING: HIGH VOLTAGE RISK. This unit interfaces with 415V/440V industrial grids. Disconnect all power sources before installation. Phase wiring (R/Y/B) must be verified with a phase rotation meter prior to connection to prevent mechanical reversal damage.

- WARNING: GSM ANTENNA REFLECTION. The GSM antenna must be securely attached to the SMA terminal before the unit is powered. Operating the SIM800L module without an antenna causes permanent RF stage failure due to signal reflection.

- CAUTION: RELAY CONTACT LIMITS. The internal relays are designed for signaling and control logic. For motors exceeding the starter’s direct rating, the device must only be used to drive the coils of industrial contactors.

- CAUTION: PROTECTION THRESHOLDS. Incorrect parameter settings (e.g., setting Overload or Dry Run thresholds outside of the motor’s nameplate specifications) will disable the protective fail-safes and may lead to motor winding burnout.

A verified, safe installation is the mandatory foundation for all subsequent hardware operations.

--------------------------------------------------------------------------------

## 3. PRODUCT OVERVIEW

The QBIT-PIC18F-GSM is a high-performance industrial motor management system powered by the Microchip® PIC18F26K22 microcontroller. It is specifically engineered to solve the challenges of remote motor management in environments such as agricultural irrigation, water treatment, and factory automation. By integrating the SIM800L GSM module, the device provides global reach, allowing operators to start, stop, and monitor assets via SMS regardless of distance.

For industrial operators, this device offers a robust alternative to manual starters. It provides a comprehensive suite of digital protections—including high/low voltage monitoring, overload detection, and dry run prevention—all governed by 10-bit ADC precision. The combination of local control (Rotary Encoder and 4-line LCD) and remote GSM accessibility ensures that motor status is always transparent and manageable.

--------------------------------------------------------------------------------

## 4. TECHNICAL SPECIFICATIONS

The following specifications define the operational boundaries of the device, ensuring compatibility with standard industrial power environments and high-precision monitoring requirements.

| Parameter | Specification |
| --- | --- |
| Microcontroller | Microchip® PIC18F26K22 (8-bit) |
| Clock Frequency | 20 MHz (External Crystal) |
| Supply Voltage Range | 100V – 600V AC (Calibrated via 390.4 Scale Factor) |
| ADC Resolution | 10-bit (1024 levels) for high-precision sensing |
| Phase Support | Software selectable: 2-Phase (2P) or 3-Phase (3P) |
| Current Range | Up to 300A (Scaleable via external Current Transformers) |
| GSM Module | SIM A767C0 Quad-band (9600 Baud UART) |
| User Interface | 20x4 Alphanumeric LCD with 3-Wire Interface |
| Menu Items | 18-Point Programmable Menu System |
| Data Retention | Internal Non-volatile EEPROM |

--------------------------------------------------------------------------------

## 5. HARDWARE COMPONENTS & WIRING

The hardware architecture is designed for modularity and rapid diagnostic assessment.

- LCD Display: 4-line screen connected via pins B0 (Enable), C3 (Data), and C4 (Clock).

- Rotary Encoder: Navigation and value adjustment via pins C5 (A), A4 (B), and B6 (Switch).

- KEY1 (ON/Inc): Connected to PIN_B3. Used for manual motor start and parameter incrementing.

- KEY2 (OFF/Dec): Connected to PIN_B2. Used for manual motor stop and parameter decrementing.

- R/Y/B Status LEDs: Indicators for phase health located on pins C0, C1, and B1 respectively.

- Relay Pins: Output pins B4 (ON Relay) and B5 (OFF Relay) for contactor control.

- GSM Connector: SMA female connector for external antenna.

- ADC Inputs: 10-bit inputs (AN0–AN4, AN14) for voltage and CT current sensing.

### Simple Wiring Checklist

- [ ] Connect R, Y, and B phases to sensing terminals (Verify 415V nominal).

- [ ] Pass motor power leads through Current Transformers (CT).

- [ ] Connect CT outputs to the designated ADC input terminals.

- [ ] CRITICAL: Secure GSM antenna to SMA port before SIM insertion.

--------------------------------------------------------------------------------

## 6. FIRST-TIME SETUP

A systematic initialization ensures the firmware correctly maps the motor's electrical profile.

- Initial Power-on: Apply power; the device performs an internal self-test.

- Splash Verification: Confirm the screen displays "NEW QBITRONICS" followed by "DIGITAL STARTER."

- Phase Sequence Check: Observe "Seq. Checking..."; ensure phases are correctly detected as RYB.

- Admin Registration: Use the GSM Menu (Item 16) to save the primary Admin phone number to Slot 1.

- Parameter Thresholds: Set High/Low Voltage limits and Overload Amperage in Menu 6.

- Operating Mode: Select between Manual or Timer mode in Menu 10.

- Functional Test: Perform a local start via KEY1 and verify current readings on the LCD.

--------------------------------------------------------------------------------

## 7. LCD DISPLAY GUIDE

The LCD interface provides real-time transparency into the firmware's measurement logic.

### State: Motor Running

R:230V Y:231V B:229V

R:10.5 Y:10.4 B:10.6

MOTOR STATUS: ON

RUNNING...

- Status Meaning: Motor is energized. Current readings (R, Y, B) represent actual load per phase.

- Required Action: None.

### State: Motor OFF

R:232V Y:230V B:231V

R:0.0  Y:0.0  B:0.0

MOTOR STATUS: OFF

READY...

- Status Meaning: Power is available but the motor is idle.

- Required Action: Initiate start via KEY1 or GSM command.

### State: Fault Trip

*** FAULT DETECTED ***

Motor OFF Due to

LOW VOLTAGE TRIP

RESET REQUIRED

- Status Meaning: Protection logic has triggered a shutdown.

- Required Action: Verify line voltage; press KEY2 to reset fault state.

--------------------------------------------------------------------------------

## 8. PHYSICAL CONTROLS

Local interaction is managed via tactile inputs for immediate responsive control.

- KEY1: Manually triggers the "ON" relay. In menus, increases numeric values.

- KEY2: Manually triggers the "OFF" relay. In menus, decreases numeric values.

- Encoder Rotate: Primary navigation for the 18-point menu system.

- Encoder Press: Confirms selections or enters sub-menus.

- Combination (KEY2 + Encoder Press): Security shortcut to enter the system configuration menu.

--------------------------------------------------------------------------------

## 9. THE MENU SYSTEM

The 18-point menu provides granular access to the PIC18F firmware settings.

| No. | Menu Name | Function | Range/Options | Recommended | Safety Warning |
| --- | --- | --- | --- | --- | --- |
| 1 | Phase Setting | Sets logic for 2P or 3P operation. | 2P / 3P | 3P | Wrong setting results in false phase-loss trips. |
| 2 | Juice Control | Global Protection Enable/Disable. | Enable / Disable | Enable | WARNING: Disabling removes all fail-safes. |
| 3 | Power On Delay | Stabilization delay after power-up. | 0 – 999s | 10s | Prevents starting on grid transients. |
| 4 | Set On Time | Duration of "Start" relay pulse. | 0 – 60s | 3s | Excessive time may burn contactor coils. |
| 5 | Star Delta Dly | Transition delay for Star-Delta. | 0 – 60s | 3s | Must allow motor to reach 75% speed. |
| 6 | Volt Setting | High/Low Voltage & Overload limits. | 100V–600V | Nameplate | Must be set precisely for protection. |
| 7 | Dry Run Delay | Delay before dry run shutdown. | 0 – 999s | 30s | Prevents nuisance trips during priming. |
| 8 | Dryrun Restart | Auto-restart delay for dry run. | 0 – 999s | 90s | Allows well/source recovery. |
| 9 | Dryrun Trip | Current threshold for dry run. | 0 – 100A | Load-based | Too low will fail to detect dry running. |
| 10 | Manual/Timer | Selects primary control logic. | Manual/Timer | Manual | Verify timer slots before enabling. |
| 11 | Cyclic Timer | Configures 5 ON/OFF time slots. | 5 Slots | User | Overlaps will cause logic conflicts. |
| 12 | Repeat Timer | Enables looping of the 5 slots. | Enable/Disable | Disable | Can lead to excessive cycling if enabled. |
| 13 | Auto Start | Auto-restart on power restoration. | Enable/Disable | Disable | Caution: Motor may start unexpectedly. |
| 14 | Unbalanced Trp | Threshold for phase current variance. | 0 – 100% | 30% | Too low causes trips on minor grid noise. |
| 15 | CT Type | Matches ADC logic to CT ratio. | 5A – 300A | Match HW | Incorrect ratio yields false Amperage data. |
| 16 | GSM Setting | Enables SIM800L communication. | Enable/Disable | Enable | Do not enable without antenna attached. |
| 17 | PI Test | Polarization Index insulation test. | 1m/10m IR | - | PI >= 2.0: GOOD; PI < 1.0: BAD INSULATION. |
| 18 | Exit | Return to monitoring screen. | - | - | Changes are saved to EEPROM on exit. |

--------------------------------------------------------------------------------

## 10. OPERATING MODES

### Manual Mode

The device operates based on KEY1/KEY2 or SMS commands. If Auto Start is enabled (Menu 13), the motor will automatically restart after the "Power On Delay" once power is restored, assuming no faults are present.

### Timer Mode

Timer mode executes a 5-slot schedule (ON/OFF durations).

- Persistence: The firmware utilizes EEPROM addresses 0x97 to 0x9B to save the active slot and countdown time (timer_h, timer_m).

- Resume Logic: After a power failure, the device reloads these values and resumes the cycle exactly where it was interrupted, ensuring irrigation or industrial cycles are maintained.

--------------------------------------------------------------------------------

## 11. PROTECTION FEATURES

The system employs real-time monitoring to prevent mechanical and electrical failure.

- High/Low Voltage: Monitors RMS voltage. Trip occurs if limits in Menu 6 are breached for >1 second.

- Overload Protection: Compares phase currents (AR, AY, AB) against the over_c limit. Requires manual reset.

- Dry Run Protection: Detects current drop below the drya threshold. Triggers "Dryrun Restart" timer (Menu 8) for automated recovery attempts.

- Unbalanced Phase: Logic compares max/min phase variance. If (Max - Min) / Average > ub_limit (Default 30%), the system trips to protect motor windings.

--------------------------------------------------------------------------------

## 12. GSM AND SMS COMMANDS

MANDATORY: Slot 1 (Admin) must be registered via the local menu before remote commands are accepted.

| Command | Action | Authorized Sender | Device Response |
| --- | --- | --- | --- |
| #ON | Turns Motor ON | Slots 1–5 | "MOTOR turned ON" |
| #OF | Turns Motor OFF | Slots 1–5 | "MOTOR turned OFF" |
| $S | Status Query | Admin Only | Detailed Volt/Amp/State Report |
| ?N | Show Stored Numbers | Admin Only | List of all 5 slots |
| #n1[num] | Save Admin Number | Admin Only | "Admin Number Saved" |
| #n2-5[num] | Save User Number | Admin Only | "Saved Number" |
| #EN[2-5] | Enable User Slot | Admin Only | "Slot X Enabled" |
| #DN[2-5] | Disable User Slot | Admin Only | "Slot X Disabled" |
| %M | Check Motor Status | Slots 1–5 | "MOTOR Status: [ON/OFF]" |
| @2P | Switch to 2-Phase | Admin Only | Logic updated to 2-Phase |
| @3P | Switch to 3-Phase | Admin Only | Logic updated to 3-Phase |

--------------------------------------------------------------------------------

## 13. STARTUP SEQUENCE

- Splash Screen 1: Displays "NEW QBITRONICS".

- Splash Screen 2: Displays "DIGITAL STARTER".

- EEPROM Load: Firmware retrieves saved thresholds, CT ratios, and GSM flags.

- GSM Initialization: SIM800L is initialized (AT+CMGF=1) and memory is cleared (AT+CMGD=1,4).

- Phase Check: Verify phase presence and sequence.

- Power-On Delay: Counts down the seconds set in Menu 3.

- Timer Resume: Reloads saved timer state from EEPROM if valid.

--------------------------------------------------------------------------------

## 14. TROUBLESHOOTING

| Problem Observed | Recommended Solution |
| --- | --- |
| Motor non-start | Check LCD for "Fault Trip". Ensure phase sequence is RYB. |
| GSM Unresponsive | Check antenna and SIM signal. Verify Slot 1 Admin number. |
| Recurring Trips | Check Menu 14 Unbalanced Trp limit; verify CT ratio in Menu 15. |
| RF Stage Failure | Solution: Never power the unit without the SMA antenna securely attached to prevent signal reflection damage. |
| Wrong Amp Readings | Ensure CT Type in Menu 15 matches the physical hardware ratio. |

--------------------------------------------------------------------------------

## 15. WARRANTY AND SUPPORT

QBITRONICS provides a one-year limited warranty against manufacturing defects. The PIC18F firmware ensures all settings are permanently stored in EEPROM, preventing data loss during power cycles.

Manufacturer Contact Details: [Placeholder for Manufacturer Address] [Placeholder for Technical Support Phone] [Placeholder for Support Email]

The QBIT-PIC18F-GSM is the ultimate solution for intelligent, remote industrial motor control.